Installation:

- Verify that roof surface is smooth and clean to extent needed to receive materials.

- Review approved final drawings to determine the locations of EcoCurb Supports.

- Clean surfaces to receive EcoCurb Supports removing any loose gravel and any foreign matter before setting EcoCurb Supports.

- Accurately locate and align pre-fabricated EcoCurb supports in locations specified as per approved shop drawings or as required herein and by site conditions to limit pipe and/or conduit deflection to L/240, not to exceed 10' (3m) on center. If Isolation pads are required, place under each EcoCurb Support.

- Should the roofing manufacturer require a separation sheet between the roof and the EcoCurb Support system, place a separation sheet or protective pad conforming to the existing roof manufacturer’s system under each EcoCurb Support. Do not adhere to the roof system or to EcoCurb Support.

- Repeat until all supports supplied are installed in accordance with approved shop drawings.

- Remove any unused materials and packaging from job site.

| Model | Dimensions | Weight |
| --- | --- | --- |
|  | A | B |  |
| REC9SA REC13SA | 9”/22.86cm 13”/33.02cm | 8”/20.32cm 12”/30.48cm | 11 lb/4.99 kg 15 lb/6.80 kg |

REC-SA – Rubber EcoCurb Support with Adjustable Strut – Is designed specifically for use on rooftop without adhesive, roof penetrations, flashings or damage to roofing system.  Utilized to support conduit or pipe sizes up to 8".  Height of channel can be adjusted along the length of the 12” threaded rods.  Strut clamps are suggested to hold piping.

Materials

EcoCurb:  Manufactured from Recycled Rubber, Vulcanized.

LEED:  100% recycled pre-consumer rubber

Frame:  1-5/8” X 1-5/8” 12 ga. channel (ASTM A653) - available in Pre-Galvanized Zinc coated, Hot-Dip Galvanized or Stainless Steel finishes.

Hardware:  1/2” Threaded Rods (12” high); 1/2” Nuts & Washers available in Pre-Galvanized Zinc coated, Hot-Dip Galvanized or Stainless Steel finishes.

Accessories:  Strut Clamps; Protection Pads

This print/image and design and detail shown hereon is the property of Advanced Support Products, Inc. This print is furnished with the understanding that it is not to be reproduced without permission, and must be returned upon demand.  All rights of design and invention are reserved by Advanced Support Products.      Patents #5816554 ;  #6229497;  #6427965; #6448497; #6578827  © 2010

Specification Sheet

REC-SA

Rubber EcoCurb with Adjustable Strut